## Sheet2
1 | Motor Type | SM/BA/BM | SMX | SMX | SMX | SMX | SMX | SMX | SMX | SMX | SMX | SMX | SMX | SMX | SMX | SMX | SMX | SMX | SMX | SMX | SMX | SMX
2 | Power Rating | (kW) | 0.12 | 0.18 | 0.25 | 0.37 | 0.55 | 0.75 | 1.1 | 1.5 | 2.2 | 3.7 | 5.5 | 7.5 | 11 | 15 | 18.5 | 22 | 30 | 37 | 45 | 55
3 | No. of Poles |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
4 | Frame Size |  | 63A | 63B | 71A | 71B | 80A | 80B | 90S | 90L | 100L | 112M | 132S | 132M | 160M | 160L | 180M | 180L | 200L | 225S | 225M | 250M
5 | Mounting |  | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5
6 | Rated Voltage | (V) | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415
7 | Stator Connection | (Δ/Υ) | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y
8 | Rated Frequency | (Hz) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
9 | Rated Current | (Amps) | Italy | Italy | Italy | 1.8 / 1.1 | Italy | 3.5 / 2.0 | 4.5 / 2.6 | 6.1 / 3.5 | 8.3 / 4.8 | 13.3 / 7.7 | 19.1 / 11.0 | 25.8 / 14.9 | 38.6 / 22.3 | 52.3 / 30.2 | 64.2 / 37.1 | 72.1 / 41.7 | 92.0 / 53.2 | 114.5 / 66.2 | 137.2 / 79.3 | 167.1 / 96.6
10 | Rated Speed | (rpm) | Italy | Italy | Italy | 1415 | Italy | 1415 | 1428 | 1430 | 1440 | 1450 | 1457 | 1457 | 1460 | 1470 | 1475 | 1472 | 1475 | 1480 | 1480 | 1480
11 | Rated Torque | (Nm) | Italy | Italy | Italy | 2.6 | Italy | 5.06 | 7.37 | 10 | 14.5 | 24.2 | 36 | 49.2 | 71.5 | 97.4 | 119.8 | 142.4 | 194.2 | 238.7 | 290.4 | 354.9
12 | Efficiency Class |  | IE3 | IE3 | IE3 | IE3 | IE3 | IE3 | IE3 | IE3 | IE3 | IE3 | IE3 | IE3 | IE3 | IE3 | IE3 | IE3 | IE3 | IE3 | IE3 | IE3
13 | Duty Type |  | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1
14 | Insulation Class |  | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B)
15 | Degree of protection |  | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55
16 | Method of cooling |  | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411
17 | Current - Locked rotor / Rated | IA / IN | Italy | Italy | Italy | 4.5 | Italy | 5.6 | 5.7 | 6.2 | 7 | 7.1 | 7.6 | 7.9 | 9.1 | 9.1 | 9.1 | 8.6 | 8.4 | 8.5 | 8.8 | 9.8
18 | Torque - Locked rotor / Rated | MA / MN | Italy | Italy | Italy | 3.5 | Italy | 3.1 | 3.4 | 3.5 | 2.9 | 3.7 | 3.5 | 3.3 | 3.8 | 3.5 | 3.5 | 4.3 | 2.9 | 2.7 | 2.8 | 3.2
19 | Torque - Breakdown / Rated | Mk / MN | Italy | Italy | Italy | 3.6 | Italy | 3.2 | 3.9 | Italy | Italy | 4.5 | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy
20 | Efficiency | 100% | Italy | Italy | Italy | 77.8 | Italy | 82.5 | 84.1 | 85.3 | 86.7 | 88.8 | 89.6 | 90.4 | 91.4 | 92.1 | 92.6 | 93 | 93.6 | 93.9 | 94.2 | 94.6
21 |  | 75% | Italy | Italy | Italy | 77.2 | Italy | 82.8 | 84.3 | 85.2 | 87 | 88.9 | 91.1 | 90.7 | 91.6 | 92.3 | 92.6 | 93 | 93.4 | 94.4 | 94.7 | 95.1
22 |  | 50% | Italy | Italy | Italy | 73.8 | Italy | 81.2 | 82.6 | 83.6 | 85.4 | 87.6 | 89.3 | 90.2 | 91 | 91.8 | 91.7 | 92 | 93.4 | 91.9 | 92.2 | 92.6
23 | Power Factor | 100% | Italy | Italy | Italy | 0.63 | Italy | 0.67 | 0.73 | 0.74 | 0.76 | 0.76 | 0.8 | 0.82 | 0.78 | 0.78 | 0.78 | 0.82 | 0.87 | 0.86 | 0.87 | 0.87
24 |  | 75% | Italy | Italy | Italy | 0.53 | Italy | 0.6 | 0.64 | 0.64 | 0.67 | 0.68 | 0.74 | 0.75 | 0.71 | 0.71 | 0.72 | 0.73 | 0.84 | 0.77 | 0.78 | 0.78
25 |  | 50% | Italy | Italy | Italy | 0.41 | Italy | 0.47 | 0.5 | 0.5 | 0.54 | 0.54 | 0.62 | 0.63 | 0.59 | 0.59 | 0.59 | 0.68 | 0.75 | 0.72 | 0.73 | 0.73
26 | Environmental condition |  | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m
27 | Locked rotor time | Hot (sec) | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy
28 |  | Cold (sec) | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy
29 | Moment of inertia | (kg.m²) | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy
30 | Bearing | DE | 6202Z | 6202Z | 6203Z | 6203Z | 6204Z | 6204Z | 6205Z | 6205Z | 6206Z | 6306Z | 6308Z | 6308Z | 6309Z | 6309Z | 6310Z | 6310Z | 6312Z | 6214Z | 6214Z | 6316Z
31 |  | NDE | 6202Z | 6202Z | 6203Z | 6203Z | 6204Z | 6204Z | 6205Z | 6205Z | 6206Z | 6306Z | 6308Z | 6308Z | 9309Z | 9309Z | 6310Z | 6310Z | 6310Z | 6312Z | 6312Z | 6314Z
32 | Bearing life time | (Hrs) | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000
33 | Lubrication type |  | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated
34 | Material | Housing | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron
35 |  | Flange | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron
36 | Motor weight | (kgs) | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy
37 | Lifting eyebolt size |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | Lifting Lug | Lifting Lug | Lifting Lug | M12 | M12 | M12 | M12 | Italy | Italy | Italy | Italy
38 | Voltage variation |  | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10%
39 | Frequency variation |  | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5%
40 | Combined variation |  | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10%
41 | Terminal box position | (Viewing from NDE) | Top | Top | Top | Top | Top | Top | Top | Top | Top | Top | Top | Top | Left Side | Left Side | Left Side | Left Side | Left Side | Left Side | Left Side | Left Side
42 | Material of terminal box |  | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium
43 | Type of terminal box |  | Std | Std | Std | Std | Std | Std | Std | Std | Std | Std | Std | Std | Std | Std | Std | Std | Std | Std | Std | Std
44 | Terminal size |  | M4 | M4 | M4 | M4 | M4 | M4 | M4 | M4 | M4 | M4 | M6 | M6 | M8 | M8 | Italy | Italy | Italy | Italy | Italy | Italy
45 | No of terminals |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
46 | Cable entry thread size |  | 2xM16x1.5 | 2xM16x1.5 | 2xM20x1.5 | 2xM20x1.5 | 2xM20x1.5 | 2xM20x1.5 | 2xM25x1.5 | 2xM25x1.5 | 2xM25x1.5 | 2xM25x1.5 | 2xM32x1.5 | 2xM32x1.5 | 2xM40x1.5 | 2xM40x1.5 | 2xM40x1.5 | 2xM40x1.5 | 2xM40x1.5 | 2xM50x1.5 | 2xM50x1.5 | 2xM50x1.5
47 | No. of cable glands | Nos | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
48 | Cable diameter (min - max) | mm | 5 - 10 | 5 - 10 | 6 - 12 | 6 - 12 | 6 - 12 | 6 - 12 | 13 - 18 | 13 - 18 | 13 - 18 | 13 - 18 | 18 - 25 | 18 - 25 | 22 - 32 | 22 - 32 | 22 - 32 | 22 - 32 | 22 - 32 | 32 - 38 | 32 - 38 | 32 - 38
49 | Max. Cable size | mm² | - | - | 3Cx1.5 | 3Cx1.5 | 3Cx1.5 | 3Cx1.5 | 3Cx6.0 | 3Cx6.0 | 3Cx6.0 | 3Cx6.0 | 3Cx35 | 3Cx35 | 3Cx70 | 3Cx70 | 3Cx70 | 3Cx70 | 3Cx70 | 3Cx120 | 3Cx120 | 3Cx120
50 | Painting cycle |  | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish
51 | Color / Paint Shade |  | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue
52 | Reference standard |  | IS : 12615 / IEC 60034-2 | IS : 12615 / IEC 60034-2 | IS : 12615 / IEC 60034-2 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-0 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1
53 | Vibration severity grade |  | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard)
54 | Sound pressure level - 50Hz | dB(A) | 42 | 42 | 45 | 45 | 47 | 47 | 55 | 55 | 57 | 61 | 62 | 62 | 63 | 63 | 64 | 64 | 66 | 68 | 68 | 70