## Sheet2
| Motor Type | SM/BA/BM | BMX | BMX | BMX | BMX | BMX | BMX | BMX | BMX | BMX | BMX | BMX | BMX | BMX | BMX | BMX | BMX | BMX | BMX | BMX | BMX
2 | Power Rating | (kW) | 0.12 | 0.18 | 0.25 | 0.37 | 0.55 | 0.75 | 1.1 | 1.5 | 2.2 | 3.7 | 5.5 | 7.5 | 11 | 15 | 18.5 | 22 | 30 | 37 | 45 | 55
3 | No. of Poles |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
4 | Frame Size |  | 63A | 63B | 71A | 71B | 80A | 80B | 90S | 90L | 100L | 112M | 132S | 132M | 160M | 160L | 180M | 180L | 200L | 225S | 225M | 250M
5 | Mounting |  | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5 | IM B5
6 | Rated Voltage | (V) | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415 | 240 / 415
7 | Stator Connection | (Δ/Υ) | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y
8 | Rated Frequency | (Hz) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
9 | Rated Current | (Amps) | 0.62 / 0.36 | 1.1 / 0.58 | 1.31 / 0.76 | 1.7 / 0.98 | 2.45 / 1.14 | 3.3 / 1.9 | 4.3 / 2.5 | 6.09 / 3.5 | 8.2 / 4.7 | 14.0 / 8.1 | 19.1 / 11.1 | 26.0 / 15.0 | 37.7 / 21.8 | 51.4 / 29.7 | 64.55 / 37.1 | 72.5 / 41.7 | 92.568 / 53.2 | 115.2 / 66.2 | 137.9 / 79.3 | 168 / 96.8
10 | Rated Speed | (rpm) | 1300 | 1340 | 1400 | 1385 | 1408 | 1415 | 1420 | 1430 | 1446 | 1456 | 1453 | 1457 | 1460 | 1460 | 1475 | 1472 | 1475 | 1480 | 1480 | 1480
11 | Rated Torque | (Nm) | 0.8 | 1.3 | 1.7 | 2.6 | 3.6 | 5 | 7.5 | 10 | 14.7 | 24.3 | 36.1 | 49.3 | 71.9 | 98.3 | 119.8 | 142.4 | 194.2 | 238.7 | 290.4 | 354.88
12 | Efficiency Class |  | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2
13 | Duty Type |  | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1
14 | Insulation Class |  | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B) | 155(F) utilized to 130(B)
15 | Degree of protection |  | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55 | IP 55
16 | Method of cooling |  | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411 | TEFC / IC411
17 | Current - Locked rotor / Rated | IA / IN | 1 | 1.6 | 2.7 | 4 | 4.9 | 8.7 | 14.5 | 21 | 37.1 | 64 | 86.6 | 109.5 | 128.6 | 184.2 | 337.6 | 358 | 477 | 546 | 377 | 948
18 | Torque - Locked rotor / Rated | MA / MN | 1.8 | 2.9 | 3.4 | 6.5 | 8.6 | 14.5 | 20.3 | 35 | 51.5 | 111.8 | 122.7 | 172.6 | 172.6 | 294.9 | 299.5 | 404 | 667 | 600 | 800 | 887.2
19 | Torque - Breakdown / Rated | Mk / MN | 2.6 | 2.7 | 4.3 | 6.8 | 9.7 | 15.5 | 23.3 | 38 | 63.2 | 121.5 | 130 | 167.6 | 186.9 | 304.7 | 311.4 | 413 | 730 | 664 | 820 | 922.7
20 | Efficiency | 100% | 60.1 | 64.7 | 68.5 | 72.7 | 76.5 | 79.6 | 81.5 | 82.8 | 85.5 | 86.3 | 87.8 | 88.7 | 89.8 | 89.8 | 92.6 | 91.6 | 92.3 | 92.7 | 93.1 | 93.5
21 |  | 75% | 59.6 | 62.5 | 66.3 | 73 | 76.1 | 81.3 | 80.9 | 81.5 | 86.2 | 86.7 | 88.3 | 88.6 | 90.3 | 90.6 | 92.5 | 91.1 | 93.4 | 92.7 | 93.6 | 93.5
22 |  | 50% | 53.2 | 51.4 | 61.4 | 70.3 | 72.5 | 79.7 | 79.3 | 79.1 | 84.5 | 84.7 | 87.3 | 87.5 | 90 | 90.2 | 91.4 | 90.6 | 93.3 | 92.1 | 92.8 | 93
23 | Power Factor | 100% | 0.7 | 0.7 | 0.69 | 0.74 | 0.7 | 0.71 | 0.77 | 0.76 | 0.77 | 0.75 | 0.82 | 0.8 | 0.81 | 0.81 | 0.77 | 0.81 | 0.85 | 0.84 | 0.87 | 0.87
24 |  | 75% | 0.59 | 0.61 | 0.6 | 0.65 | 0.59 | 0.58 | 0.73 | 0.68 | 0.69 | 0.65 | 0.77 | 0.74 | 0.77 | 0.76 | 0.71 | 0.76 | 0.84 | 0.79 | 0.84 | 0.84
25 |  | 50% | 0.45 | 0.46 | 0.45 | 0.5 | 0.46 | 0.45 | 0.6 | 0.54 | 0.56 | 0.5 | 0.65 | 0.63 | 0.66 | 0.65 | 0.59 | 0.64 | 0.8 | 0.7 | 0.76 | 0.79
26 | Environmental condition |  | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m | + 40°C / 1000m
27 | Locked rotor time | Hot (sec) | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy
28 |  | Cold (sec) | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy
29 | Moment of inertia | (kg.m²) | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy
30 | Bearing | DE | 6202Z | 6202Z | 6203Z | 6203Z | 6204Z | 6204Z | 6205Z | 6205Z | 6206Z | 6306Z | 6308Z | 6308Z | 6309Z | 6209Z | 6210Z | 6210Z | 6312Z | 6214Z | 6214Z | 6316Z
31 |  | NDE | 6202Z | 6202Z | 6203Z | 6203Z | 6204Z | 6204Z | 6205Z | 6205Z | 6206Z | 6306Z | 6308Z | 6308Z | 6309Z | 6209Z | 6210Z | 6210Z | 6310Z | 6312Z | 6312Z | 6314Z
32 | Bearing life time | (Hrs) | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000
33 | Lubrication type |  | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated | Pre-lubricated
34 | Material | Housing | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron
35 |  | Flange | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron | Cast iron
36 | Motor weight | (kgs) | 3 | 4 | 6 | 6.5 | 10 | 10 | 15 | 16.5 | 23 | 37 | 64 | 71 | 108 | 175 | 250 | 250 | 230 | 315 | 380 | 600
37 | Lifting eyebolt size |  | - | - | - | - | - | - | - | - | - | - | - | - | M12 | M12 | M12 | M12 | M12 | M12 | M12 | M12
38 | Voltage variation |  | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10%
39 | Frequency variation |  | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5% | ±5%
40 | Combined variation |  | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10% | ±10%
41 | Terminal box position | (Viewing from NDE) | Top | Top | Top | Top | Top | Top | Top | Top | Top | Top | Top | Top | Left Side | Left Side | Left Side | Left Side | Left Side | Left Side | Left Side | Left Side
42 | Material of terminal box |  | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium | Aluminium
43 | Type of terminal box |  | Std + DM | Std + DM | Std + DM | Std + DM | Std + DM | Std + DM | Std + DM | Std + DM | Std + DM | Std + DM | Std + DM | Std + DM | Std + DM | Std + DM | Std + DM | Std + DM | Std + DM | Std | Std | Std
44 | Terminal size |  | M4 | M4 | M4 | M4 | M4 | M4 | M4 | M4 | M4 | M4 | M6 | M6 | M8 | M8 | Italy | Italy | Italy | Italy | Italy | Italy
45 | No of terminals |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
46 | Cable entry thread size |  | 2xM25x1.5 | 2xM20x1.5 | 2xM20x1.5 | 2xM20x1.5 | 2xM20x1.5 | 2xM20x1.5 | 2xM25x1.5 | 2xM25x1.5 | 2xM25x1.5 | 2xM25x1.5 | 2xM32x1.5 | 2xM32x1.5 | 2xM40x1.5 | 2xM40x1.5 | 2xM40x1.5 | 2xM40x1.5 | 2xM40x1.5 | 2xM50x1.5 | 2xM50x1.5 | 2xM50x1.5
47 | No. of cable glands | Nos | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
48 | Cable diameter (min - max) | mm | 6 - 12 | 6 - 12 | 6 - 12 | 6 - 12 | 6 - 12 | 6 - 12 | 13 - 18 | 13 - 18 | 13 - 18 | 13 - 18 | 18 - 25 | 18 - 25 | 22 - 32 | 22 - 32 | 22 - 32 | 22 - 32 | 22 - 32 | 32 - 38 | 32 - 38 | 32 - 38
49 | Max. Cable size | mm² | 3Cx1.5 | 3Cx2.5 | 3Cx1.5 | 3Cx1.5 | 3Cx1.5 | 3Cx1.5 | 3Cx6 | 3Cx6 | 3Cx6 | 3Cx6 | 3Cx35 | 3Cx35 | 3Cx70 | 3Cx70 | 3Cx70 | 3Cx70 | 3Cx70 | 3Cx120 | 3Cx120 | 3Cx120
50 | Painting cycle |  | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish | Std paint finish
51 | Color / Paint Shade |  | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue | RAL 5010 Blue
52 | Reference standard |  | IS : 12615 / IEC 60034-2 | IS : 12615 / IEC 60034-2 | IS : 12615 / IEC 60034-2 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-0 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1 | IS : 12615 / IEC 60034-1
53 | Vibration severity grade |  | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard) | A (Standard)
54 | Sound pressure level - 50Hz | dB(A) | 45 | 45 | 45 | 45 | 47 | 47 | 55 | 55 | 57 | 61 | 62 | 62 | 63 | 63 | 64 | 64 | 66 | 68 | 68 | 70
55 | Brake type | (AC / DC) | DC | DC | DC | DC | DC | DC | DC | DC | DC | DC | DC | DC | DC | DC | DC | DC | DC | DC | DC | DC
56 | Input supply voltage | (V) (AC) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240
57 | No. of Phase |  | 2ø | 2ø | 2ø | 2ø | 2ø | 2ø | 2ø | 2ø | 2ø | 2ø | 2ø | 2ø | 2ø | 2ø | 2ø | 2ø | 2ø | 2ø | 2ø | 2ø
58 | Brake coil voltage | (V) (DC) | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103
59 | Brake torque | (Nm) | 5 | 5 | 5 | 5 | 10 | 10 | 20 | 20 | 40 | 60 | 100 | 100 | 150 | 150 | 250 | 250 | 250 | 400 | 400 | 400
60 | Brake safety factor |  | >4 | >4 | 2.9 | 1.9 | 2.7 | 2 | 2.7 | 2 | 2.7 | 2.5 | 2.8 | 2 | 2.1 | 1.5 | 2 | 1.7 | 1.3 | 1.7 | 1.4 | 1.1
61 | Brake reaction time | (m.sec) | 90 | 90 | 90 | 90 | 145 | 145 | 180 | 180 | 225 | 290 | 420 | 420 | 570 | 570 | 600 | 600 | 600 | 900 | 900 | 900
62 | Brake current | (A) | 0.2 | 0.2 | 0.2 | 0.2 | 0.16 | 0.16 | 0.19 | 0.19 | 0.25 | 0.47 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.92 | 0.92 | 0.92
63 | Data Sheet No. |  | YTP | YTP | YTP | YTP | YTP | YTP | YTP | YTP | YTP | YTP | YTP | YTP | YTP | YTP | YTP | YTP | YTP | YTP | YTP | YTP
64 | PD Drg No. |  | Avl | Avl | Avl | Avl | Avl | Avl | Avl | Avl | Avl | Avl | Avl | Avl | Avl | Avl | Avl | Avl | Avl | Avl | Avl | Avl
65 | TB Drg No. |  | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy
66 | Load Vs Efficiency curve |  | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy
67 | Load Vs power factor curve |  | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy
68 | Torque speed curve |  | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy
69 | Current Vs time curve |  | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy
70 | Current Vs Speed curve |  | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy
71 | Thermal withstand curve |  | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy | Italy